## Acceptance Summary
ASHRAE 140-2023 Acceptance testing summary for eQUEST 3.65 with DOE-2.2 and DOE-2.3 versions*
Acceptance group | STD 140 Section | In-Range test count to Pass | DOE-2.2 within range count | DOE-2.2 status | DOE-2.3 within range count | DOE-2.3 status
Thermal fabric, low mass | 5-2A | 18/21 | 21/21 | Pass | 21/21 | Pass
Thermal fabric, high mass | 5-2A | 17/19 | 17/19 | Pass | 17/19 | Pass
Cooling equipment | 5-3B | 12/14 | 14/14 | Pass | 14/14 | Pass
Heating equipment | 5-4 | 5/6 | 6/6 | Pass | 6/6 | Pass
Air-side equipment | 5-5 | 48/54 | 48/54 | Pass | 48/54 | Pass
*Results for DOE-2.2-50a and DOE-2.3-50h simulation engines as contained in eQUEST-3.65. Summary prepared September 22, 2026 - JJH & Associates with significant updates and additions, to earlier published versions, by Jackson Jarboe courtesy of Karpman Consulting.

## All Comparisons
Engine | Acceptance group | Table | Case / comparison | Metric and units | Lower limit | Upper limit | Result | Status
D22 | Thermal fabric, low mass | A3-1 | Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | 3.75 | 4.98 | 4.5721 | Within range
D22 | Thermal fabric, low mass | A3-1 | Case 610 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | -0.14 | 0.29 | 0.086171 | Within range
D22 | Thermal fabric, low mass | A3-1 | Case 620 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | -0.08 | 0.4 | 0.31743 | Within range
D22 | Thermal fabric, low mass | A3-1 | Case 630 – Case 620 | Low Mass Building – Annual Heating Load (MWh/yr) | 0.02 | 0.74 | 0.40243 | Within range
D22 | Thermal fabric, low mass | A3-1 | Case 640 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | -2.17 | -1.22 | -1.729 | Within range
D22 | Thermal fabric, low mass | A3-1 | Case 660 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | -1.07 | -0.16 | -0.41855 | Within range
D22 | Thermal fabric, low mass | A3-1 | Case 670 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | 0.25 | 2.98 | 1.0147 | Within range
D22 | Thermal fabric, low mass | A3-1 | Case 680 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | -2.54 | -1.9 | -2.3451 | Within range
D22 | Thermal fabric, low mass | A3-1 | Case 685 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | 0.33 | 0.77 | 0.67384 | Within range
D22 | Thermal fabric, low mass | A3-1 | Case 695 – Case 685 | Low Mass Building – Annual Heating Load (MWh/yr) | -2.38 | -1.94 | -2.3023 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | 5 | 6.83 | 6.265 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 610 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -2.26 | -0.8 | -1.6507 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 620 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -2.24 | -1.64 | -1.7806 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 630 – Case 620 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -1.68 | -0.77 | -1.5704 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 640 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -0.56 | 0.03 | -0.3186 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 650 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -1.54 | -0.95 | -1.5083 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 660 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -3.09 | -2.5 | -2.9228 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 670 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | 0.05 | 0.84 | 0.79489 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 680 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | 0.13 | 0.87 | 0.24796 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 685 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | 2.7 | 3.31 | 3.2877 | Within range
D22 | Thermal fabric, low mass | A3-2 | Case 695 – Case 685 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -0.21 | 0.44 | -0.17996 | Within range
D22 | Thermal fabric, high mass | A3-3 | Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | 1.04 | 2.28 | 1.8322 | Within range
D22 | Thermal fabric, high mass | A3-3 | Case 900 – Case 910 | High Mass Building – Annual Heating Load (MWh/yr) | -0.52 | -0.02 | -0.28607 | Within range
D22 | Thermal fabric, high mass | A3-3 | Case 920 – Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | 1.51 | 1.92 | 1.6903 | Within range
D22 | Thermal fabric, high mass | A3-3 | Case 930 – Case 920 | High Mass Building – Annual Heating Load (MWh/yr) | 0.2 | 1.15 | 0.78727 | Within range
D22 | Thermal fabric, high mass | A3-3 | Case 940 – Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | -0.82 | -0.37 | -0.56041 | Within range
D22 | Thermal fabric, high mass | A3-3 | Case 960 – Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | 0.96 | 1.12 | 1.4922 | Above range
D22 | Thermal fabric, high mass | A3-3 | Case 980 – Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | -1.65 | -1 | -1.3465 | Within range
D22 | Thermal fabric, high mass | A3-3 | Case 985 – Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | 0.64 | 0.81 | 0.72777 | Within range
D22 | Thermal fabric, high mass | A3-3 | Case 995 – Case 985 | High Mass Building – Annual Heating Load (MWh/yr) | -1.83 | -1.07 | -1.4916 | Within range
D22 | Thermal fabric, high mass | A3-4 | Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 2.35 | 2.6 | 2.6933 | Above range
D22 | Thermal fabric, high mass | A3-4 | Case 900 – Case 910 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 0.35 | 1.74 | 1.1264 | Within range
D22 | Thermal fabric, high mass | A3-4 | Case 920 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 0.08 | 0.48 | 0.23067 | Within range
D22 | Thermal fabric, high mass | A3-4 | Case 930 – Case 920 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | -1.19 | -0.44 | -1.0291 | Within range
D22 | Thermal fabric, high mass | A3-4 | Case 940 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | -0.19 | 0.06 | -0.072689 | Within range
D22 | Thermal fabric, high mass | A3-4 | Case 950 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | -2 | -1.56 | -1.8967 | Within range
D22 | Thermal fabric, high mass | A3-4 | Case 960 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | -1.81 | -1.27 | -1.6159 | Within range
D22 | Thermal fabric, high mass | A3-4 | Case 980 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 1.09 | 1.41 | 1.1399 | Within range
D22 | Thermal fabric, high mass | A3-4 | Case 985 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 3.52 | 4.18 | 3.8604 | Within range
D22 | Thermal fabric, high mass | A3-4 | Case 995 – Case 985 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 0.63 | 1.15 | 0.68204 | Within range
D22 | Cooling equipment | A3-5 | CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 33497 | 37023 | 34859 | Within range
D22 | Cooling equipment | A3-5 | CE310 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 2671 | 6197 | 4632.6 | Within range
D22 | Cooling equipment | A3-5 | CE320 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 2610 | 6136 | 3968.7 | Within range
D22 | Cooling equipment | A3-5 | CE330 - CE320 | Annual Total Cooling Energy Consumption (kWh/yr) | -766 | 2760 | 618.3 | Within range
D22 | Cooling equipment | A3-5 | CE330 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 3697 | 7223 | 4587 | Within range
D22 | Cooling equipment | A3-5 | CE340 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 3172 | 6698 | 4450.06 | Within range
D22 | Cooling equipment | A3-5 | CE330 - CE340 | Annual Total Cooling Energy Consumption (kWh/yr) | -1393 | 2133 | 136.94 | Within range
D22 | Cooling equipment | A3-5 | CE350 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -5354 | -1828 | -3956.28 | Within range
D22 | Cooling equipment | A3-5 | CE360 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 18084 | 21610 | 19178.88 | Within range
D22 | Cooling equipment | A3-5 | CE400 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -5783 | -2179 | -3920.6 | Within range
D22 | Cooling equipment | A3-5 | CE410 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -5929 | -371 | -3097.39 | Within range
D22 | Cooling equipment | A3-5 | CE420 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -3945 | -419 | -2255.12 | Within range
D22 | Cooling equipment | A3-5 | CE430 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -4762 | -1236 | -2871.98 | Within range
D22 | Cooling equipment | A3-5 | CE440 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -3694 | -168 | -1768.08 | Within range
D22 | Heating equipment | A3-6 | HE210 | Furnace Input Energy (GJ) | 49.86 | 55.11 | 53.0602 | Within range
D22 | Heating equipment | A3-6 | HE220 - HE210 | Furnace Input Energy (GJ) | -5.48 | -0.23 | -2.5763 | Within range
D22 | Heating equipment | A3-6 | HE230 - HE220 | Furnace Input Energy (GJ) | -9.1 | -3.86 | -6.7963 | Within range
D22 | Heating equipment | A3-7 | HE210 | Heating Equipment Cumulative Fan Energy (kWh) | 279.55 | 308.98 | 302.9 | Within range
D22 | Heating equipment | A3-7 | HE220 - HE210 | Heating Equipment Cumulative Fan Energy (kWh) | -30.21 | -0.78 | -16 | Within range
D22 | Heating equipment | A3-7 | HE230 - HE220 | Heating Equipment Cumulative Fan Energy (kWh) | 186.29 | 216.78 | 196.5 | Within range
D22 | Air-side equipment | A3-8 | AE301 | Preheat‐Coil Load (kWh/h) | 2.8 | 4.2 | 3.7523 | Within range
D22 | Air-side equipment | A3-8 | AE401 | Preheat‐Coil Load (kWh/h) | 9.75 | 10.77 | 10.7773 | Above range
D22 | Air-side equipment | A3-8 | AE301 - AE401 | Preheat‐Coil Load (kWh/h) | -7.67 | -6.16 | -7.025 | Within range
D22 | Air-side equipment | A3-9 | AE201 | Heating‐Coil Load (kWh/h) | 7.94 | 8.78 | 8.6736 | Within range
D22 | Air-side equipment | A3-10 | AE205 | Cooling‐Coil Total Load (kWh/h) | 1.82 | 2.01 | 1.9198 | Within range
D22 | Air-side equipment | A3-10 | AE245 - AE205 | Cooling‐Coil Total Load (kWh/h) | 0.2 | 0.39 | 0.30071 | Within range
D22 | Air-side equipment | A3-10 | AE206 | Cooling‐Coil Total Load (kWh/h) | 2.54 | 2.85 | 2.7198 | Within range
D22 | Air-side equipment | A3-10 | AE226‐206 | Cooling‐Coil Total Load (kWh/h) | 0.55 | 0.82 | 0.66319 | Within range
D22 | Air-side equipment | A3-10 | AE305 | Cooling‐Coil Total Load (kWh/h) | 8.77 | 9.85 | 8.9617 | Within range
D22 | Air-side equipment | A3-10 | AE305 - AE405 | Cooling‐Coil Total Load (kWh/h) | 4.55 | 5.75 | 4.8193 | Within range
D22 | Air-side equipment | A3-10 | AE345 - AE305 | Cooling‐Coil Total Load (kWh/h) | -0.15 | 0.79 | 0.39959 | Within range
D22 | Air-side equipment | A3-10 | AE345 - AE445 | Cooling‐Coil Total Load (kWh/h) | 4.76 | 6.01 | 5.1566 | Within range
D22 | Air-side equipment | A3-10 | AE306 | Cooling‐Coil Total Load (kWh/h) | 13.65 | 15.08 | 13.99 | Within range
D22 | Air-side equipment | A3-10 | AE306 - AE406 | Cooling‐Coil Total Load (kWh/h) | 5.42 | 6.86 | 5.855 | Within range
D22 | Air-side equipment | A3-10 | AE326 - AE306 | Cooling‐Coil Total Load (kWh/h) | 5.68 | 7.12 | 5.8793 | Within range
D22 | Air-side equipment | A3-10 | AE326 - AE426 | Cooling‐Coil Total Load (kWh/h) | 11.21 | 12.65 | 11.0869 | Below range
D22 | Air-side equipment | A3-10 | AE405 | Cooling‐Coil Total Load (kWh/h) | 3.9 | 4.31 | 4.1423 | Within range
D22 | Air-side equipment | A3-10 | AE445 - AE405 | Cooling‐Coil Total Load (kWh/h) | -0.15 | 0.26 | 0.062368 | Within range
D22 | Air-side equipment | A3-10 | AE406 | Cooling‐Coil Total Load (kWh/h) | 7.81 | 8.82 | 8.1351 | Within range
D22 | Air-side equipment | A3-10 | AE426 - AE406 | Cooling‐Coil Total Load (kWh/h) | 0.2 | 1.02 | 0.64739 | Within range
D22 | Air-side equipment | A3-11 | AE205 | Cooling‐Coil Sensible Load (kWh/h) | 1.82 | 2.01 | 1.9198 | Within range
D22 | Air-side equipment | A3-11 | AE245 - AE205 | Cooling‐Coil Sensible Load (kWh/h) | 0.2 | 0.39 | 0.30071 | Within range
D22 | Air-side equipment | A3-11 | AE206 | Cooling‐Coil Sensible Load (kWh/h) | 1.62 | 1.79 | 1.6981 | Within range
D22 | Air-side equipment | A3-11 | AE226‐206 | Cooling‐Coil Sensible Load (kWh/h) | -0.23 | -0.06 | -0.17015 | Within range
D22 | Air-side equipment | A3-11 | AE305 | Cooling‐Coil Sensible Load (kWh/h) | 8.77 | 9.85 | 8.9617 | Within range
D22 | Air-side equipment | A3-11 | AE305 - AE405 | Cooling‐Coil Sensible Load (kWh/h) | 4.55 | 5.75 | 4.8193 | Within range
D22 | Air-side equipment | A3-11 | AE345 - AE305 | Cooling‐Coil Sensible Load (kWh/h) | -0.15 | 0.79 | 0.39959 | Within range
D22 | Air-side equipment | A3-11 | AE345 - AE445 | Cooling‐Coil Sensible Load (kWh/h) | 4.76 | 6.01 | 5.1566 | Within range
D22 | Air-side equipment | A3-11 | AE306 | Cooling‐Coil Sensible Load (kWh/h) | 8.3 | 9.37 | 8.5334 | Within range
D22 | Air-side equipment | A3-11 | AE306 - AE406 | Cooling‐Coil Sensible Load (kWh/h) | 4.64 | 5.73 | 4.9163 | Within range
D22 | Air-side equipment | A3-11 | AE326 - AE306 | Cooling‐Coil Sensible Load (kWh/h) | -0.91 | -0.01 | -0.4551 | Within range
D22 | Air-side equipment | A3-11 | AE326 - AE426 | Cooling‐Coil Sensible Load (kWh/h) | 4.27 | 5.31 | 4.5115 | Within range
D22 | Air-side equipment | A3-11 | AE405 | Cooling‐Coil Sensible Load (kWh/h) | 3.9 | 4.31 | 4.1423 | Within range
D22 | Air-side equipment | A3-11 | AE445 - AE405 | Cooling‐Coil Sensible Load (kWh/h) | -0.15 | 0.26 | 0.062368 | Within range
D22 | Air-side equipment | A3-11 | AE406 | Cooling‐Coil Sensible Load (kWh/h) | 3.45 | 3.82 | 3.6171 | Within range
D22 | Air-side equipment | A3-11 | AE426 - AE406 | Cooling‐Coil Sensible Load (kWh/h) | -0.22 | 0.14 | -0.050352 | Within range
D22 | Air-side equipment | A3-12 | AE301 | Zone 1 Reheat‐Coil Load (kWh/h) | 7.23 | 8.1 | 7.6854 | Within range
D22 | Air-side equipment | A3-12 | AE401 | Zone 1 Reheat‐Coil Load (kWh/h) | 4.27 | 4.72 | 4.5654 | Within range
D22 | Air-side equipment | A3-12 | AE301 - AE401 | Zone 1 Reheat‐Coil Load (kWh/h) | 2.7 | 3.6 | 3.1199 | Within range
D22 | Air-side equipment | A3-12 | AE305 | Zone 1 Reheat‐Coil Load (kWh/h) | 1.92 | 2.46 | 2.0745 | Within range
D22 | Air-side equipment | A3-12 | AE345 - AE305 | Zone 1 Reheat‐Coil Load (kWh/h) | -0.11 | 0.11 | 0.015894 | Within range
D22 | Air-side equipment | A3-12 | AE306 | Zone 1 Reheat‐Coil Load (kWh/h) | 1.92 | 2.48 | 2.1101 | Within range
D22 | Air-side equipment | A3-12 | AE326 - AE306 | Zone 1 Reheat‐Coil Load (kWh/h) | -0.11 | 0.11 | 0.019982 | Within range
D22 | Air-side equipment | A3-12 | AE405 | Zone 1 Reheat‐Coil Load (kWh/h) | 0 | 0 | 0 | Skipped
D22 | Air-side equipment | A3-12 | AE406 | Zone 1 Reheat‐Coil Load (kWh/h) | 0 | 0 | 0 | Skipped
D22 | Air-side equipment | A3-13 | AE301 | Zone 2 Reheat‐Coil Load (kWh/h) | 7.77 | 8.81 | 8.3557 | Within range
D22 | Air-side equipment | A3-13 | AE401 | Zone 2 Reheat‐Coil Load (kWh/h) | 4.63 | 5.12 | 4.9963 | Within range
D22 | Air-side equipment | A3-13 | AE301 - AE401 | Zone 2 Reheat‐Coil Load (kWh/h) | 2.87 | 3.93 | 3.3594 | Within range
D22 | Air-side equipment | A3-13 | AE305 | Zone 2 Reheat‐Coil Load (kWh/h) | 2.02 | 2.71 | 2.2255 | Within range
D22 | Air-side equipment | A3-13 | AE345 - AE305 | Zone 2 Reheat‐Coil Load (kWh/h) | -0.12 | 0.12 | 0.017664 | Within range
D22 | Air-side equipment | A3-13 | AE306 | Zone 2 Reheat‐Coil Load (kWh/h) | 2.02 | 2.74 | 2.2687 | Within range
D22 | Air-side equipment | A3-13 | AE326 - AE306 | Zone 2 Reheat‐Coil Load (kWh/h) | -0.12 | 0.12 | 0.024953 | Within range
D22 | Air-side equipment | A3-13 | AE405 | Zone 2 Reheat‐Coil Load (kWh/h) | 0 | 0 | 0 | Skipped
D22 | Air-side equipment | A3-13 | AE406 | Zone 2 Reheat‐Coil Load (kWh/h) | 0 | 0 | 0 | Skipped
D23 | Thermal fabric, low mass | A3-1 | Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | 3.75 | 4.98 | 4.3519 | Within range
D23 | Thermal fabric, low mass | A3-1 | Case 610 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | -0.14 | 0.29 | 0.082361 | Within range
D23 | Thermal fabric, low mass | A3-1 | Case 620 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | -0.08 | 0.4 | 0.31098 | Within range
D23 | Thermal fabric, low mass | A3-1 | Case 630 – Case 620 | Low Mass Building – Annual Heating Load (MWh/yr) | 0.02 | 0.74 | 0.391 | Within range
D23 | Thermal fabric, low mass | A3-1 | Case 640 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | -2.17 | -1.22 | -1.7123 | Within range
D23 | Thermal fabric, low mass | A3-1 | Case 660 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | -1.07 | -0.16 | -0.42001 | Within range
D23 | Thermal fabric, low mass | A3-1 | Case 670 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | 0.25 | 2.98 | 1.003 | Within range
D23 | Thermal fabric, low mass | A3-1 | Case 680 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | -2.54 | -1.9 | -2.3087 | Within range
D23 | Thermal fabric, low mass | A3-1 | Case 685 – Case 600 | Low Mass Building – Annual Heating Load (MWh/yr) | 0.33 | 0.77 | 0.7093 | Within range
D23 | Thermal fabric, low mass | A3-1 | Case 695 – Case 685 | Low Mass Building – Annual Heating Load (MWh/yr) | -2.38 | -1.94 | -2.285 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | 5 | 6.83 | 6.2635 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 610 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -2.26 | -0.8 | -1.6525 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 620 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -2.24 | -1.64 | -1.7873 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 630 – Case 620 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -1.68 | -0.77 | -1.5769 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 640 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -0.56 | 0.03 | -0.3315 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 650 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -1.54 | -0.95 | -1.5042 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 660 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -3.09 | -2.5 | -2.9251 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 670 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | 0.05 | 0.84 | 0.78873 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 680 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | 0.13 | 0.87 | 0.27698 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 685 – Case 600 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | 2.7 | 3.31 | 3.278 | Within range
D23 | Thermal fabric, low mass | A3-2 | Case 695 – Case 685 | Low Mass Building – Annual Sensible Cooling Load (MWh/yr) | -0.21 | 0.44 | -0.1656 | Within range
D23 | Thermal fabric, high mass | A3-3 | Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | 1.04 | 2.28 | 1.6677 | Within range
D23 | Thermal fabric, high mass | A3-3 | Case 900 – Case 910 | High Mass Building – Annual Heating Load (MWh/yr) | -0.52 | -0.02 | -0.27024 | Within range
D23 | Thermal fabric, high mass | A3-3 | Case 920 – Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | 1.51 | 1.92 | 1.6437 | Within range
D23 | Thermal fabric, high mass | A3-3 | Case 930 – Case 920 | High Mass Building – Annual Heating Load (MWh/yr) | 0.2 | 1.15 | 0.77203 | Within range
D23 | Thermal fabric, high mass | A3-3 | Case 940 – Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | -0.82 | -0.37 | -0.51586 | Within range
D23 | Thermal fabric, high mass | A3-3 | Case 960 – Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | 0.96 | 1.12 | 1.4166 | Above range
D23 | Thermal fabric, high mass | A3-3 | Case 980 – Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | -1.65 | -1 | -1.2592 | Within range
D23 | Thermal fabric, high mass | A3-3 | Case 985 – Case 900 | High Mass Building – Annual Heating Load (MWh/yr) | 0.64 | 0.81 | 0.73422 | Within range
D23 | Thermal fabric, high mass | A3-3 | Case 995 – Case 985 | High Mass Building – Annual Heating Load (MWh/yr) | -1.83 | -1.07 | -1.4473 | Within range
D23 | Thermal fabric, high mass | A3-4 | Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 2.35 | 2.6 | 2.7135 | Above range
D23 | Thermal fabric, high mass | A3-4 | Case 900 – Case 910 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 0.35 | 1.74 | 1.1384 | Within range
D23 | Thermal fabric, high mass | A3-4 | Case 920 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 0.08 | 0.48 | 0.21689 | Within range
D23 | Thermal fabric, high mass | A3-4 | Case 930 – Case 920 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | -1.19 | -0.44 | -1.0358 | Within range
D23 | Thermal fabric, high mass | A3-4 | Case 940 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | -0.19 | 0.06 | -0.06712 | Within range
D23 | Thermal fabric, high mass | A3-4 | Case 950 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | -2 | -1.56 | -1.9134 | Within range
D23 | Thermal fabric, high mass | A3-4 | Case 960 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | -1.81 | -1.27 | -1.6226 | Within range
D23 | Thermal fabric, high mass | A3-4 | Case 980 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 1.09 | 1.41 | 1.2316 | Within range
D23 | Thermal fabric, high mass | A3-4 | Case 985 – Case 900 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 3.52 | 4.18 | 3.8461 | Within range
D23 | Thermal fabric, high mass | A3-4 | Case 995 – Case 985 | High Mass Building – Annual Sensible Cooling Load (MWh/yr) | 0.63 | 1.15 | 0.72484 | Within range
D23 | Cooling equipment | A3-5 | CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 33497 | 37023 | 36808.29 | Within range
D23 | Cooling equipment | A3-5 | CE310 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 2671 | 6197 | 2803.04 | Within range
D23 | Cooling equipment | A3-5 | CE320 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 2610 | 6136 | 2734.88 | Within range
D23 | Cooling equipment | A3-5 | CE330 - CE320 | Annual Total Cooling Energy Consumption (kWh/yr) | -766 | 2760 | 962.34 | Within range
D23 | Cooling equipment | A3-5 | CE330 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 3697 | 7223 | 3697.22 | Within range
D23 | Cooling equipment | A3-5 | CE340 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 3172 | 6698 | 3326.9 | Within range
D23 | Cooling equipment | A3-5 | CE330 - CE340 | Annual Total Cooling Energy Consumption (kWh/yr) | -1393 | 2133 | 370.32 | Within range
D23 | Cooling equipment | A3-5 | CE350 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -5354 | -1828 | -5166.19 | Within range
D23 | Cooling equipment | A3-5 | CE360 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | 18084 | 21610 | 18182.07 | Within range
D23 | Cooling equipment | A3-5 | CE400 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -5783 | -2179 | -4117.29 | Within range
D23 | Cooling equipment | A3-5 | CE410 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -5929 | -371 | -3599.29 | Within range
D23 | Cooling equipment | A3-5 | CE420 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -3945 | -419 | -2405.29 | Within range
D23 | Cooling equipment | A3-5 | CE430 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -4762 | -1236 | -3066.29 | Within range
D23 | Cooling equipment | A3-5 | CE440 - CE300 | Annual Total Cooling Energy Consumption (kWh/yr) | -3694 | -168 | -1921.29 | Within range
D23 | Heating equipment | A3-6 | HE210 | Furnace Input Energy (GJ) | 49.86 | 55.11 | 53.1942 | Within range
D23 | Heating equipment | A3-6 | HE220 - HE210 | Furnace Input Energy (GJ) | -5.48 | -0.23 | -2.8548 | Within range
D23 | Heating equipment | A3-6 | HE230 - HE220 | Furnace Input Energy (GJ) | -9.1 | -3.86 | -6.7225 | Within range
D23 | Heating equipment | A3-7 | HE210 | Heating Equipment Cumulative Fan Energy (kWh) | 279.55 | 308.98 | 299.3 | Within range
D23 | Heating equipment | A3-7 | HE220 - HE210 | Heating Equipment Cumulative Fan Energy (kWh) | -30.21 | -0.78 | -15.8 | Within range
D23 | Heating equipment | A3-7 | HE230 - HE220 | Heating Equipment Cumulative Fan Energy (kWh) | 186.29 | 216.78 | 202.9 | Within range
D23 | Air-side equipment | A3-8 | AE301 | Preheat‐Coil Load (kWh/h) | 2.8 | 4.2 | 3.2138 | Within range
D23 | Air-side equipment | A3-8 | AE401 | Preheat‐Coil Load (kWh/h) | 9.75 | 10.77 | 9.7059 | Below range
D23 | Air-side equipment | A3-8 | AE301 - AE401 | Preheat‐Coil Load (kWh/h) | -7.67 | -6.16 | -6.4921 | Within range
D23 | Air-side equipment | A3-9 | AE201 | Heating‐Coil Load (kWh/h) | 7.94 | 8.78 | 8.094 | Within range
D23 | Air-side equipment | A3-10 | AE205 | Cooling‐Coil Total Load (kWh/h) | 1.82 | 2.01 | 1.9399 | Within range
D23 | Air-side equipment | A3-10 | AE245 - AE205 | Cooling‐Coil Total Load (kWh/h) | 0.2 | 0.39 | 0.28605 | Within range
D23 | Air-side equipment | A3-10 | AE206 | Cooling‐Coil Total Load (kWh/h) | 2.54 | 2.85 | 2.7283 | Within range
D23 | Air-side equipment | A3-10 | AE226‐206 | Cooling‐Coil Total Load (kWh/h) | 0.55 | 0.82 | 0.68875 | Within range
D23 | Air-side equipment | A3-10 | AE305 | Cooling‐Coil Total Load (kWh/h) | 8.77 | 9.85 | 9.0986 | Within range
D23 | Air-side equipment | A3-10 | AE305 - AE405 | Cooling‐Coil Total Load (kWh/h) | 4.55 | 5.75 | 4.8169 | Within range
D23 | Air-side equipment | A3-10 | AE345 - AE305 | Cooling‐Coil Total Load (kWh/h) | -0.15 | 0.79 | 0.45454 | Within range
D23 | Air-side equipment | A3-10 | AE345 - AE445 | Cooling‐Coil Total Load (kWh/h) | 4.76 | 6.01 | 5.2217 | Within range
D23 | Air-side equipment | A3-10 | AE306 | Cooling‐Coil Total Load (kWh/h) | 13.65 | 15.08 | 14.1793 | Within range
D23 | Air-side equipment | A3-10 | AE306 - AE406 | Cooling‐Coil Total Load (kWh/h) | 5.42 | 6.86 | 5.5646 | Within range
D23 | Air-side equipment | A3-10 | AE326 - AE306 | Cooling‐Coil Total Load (kWh/h) | 5.68 | 7.12 | 6.1561 | Within range
D23 | Air-side equipment | A3-10 | AE326 - AE426 | Cooling‐Coil Total Load (kWh/h) | 11.21 | 12.65 | 11.1908 | Below range
D23 | Air-side equipment | A3-10 | AE405 | Cooling‐Coil Total Load (kWh/h) | 3.9 | 4.31 | 4.2817 | Within range
D23 | Air-side equipment | A3-10 | AE445 - AE405 | Cooling‐Coil Total Load (kWh/h) | -0.15 | 0.26 | 0.049707 | Within range
D23 | Air-side equipment | A3-10 | AE406 | Cooling‐Coil Total Load (kWh/h) | 7.81 | 8.82 | 8.6147 | Within range
D23 | Air-side equipment | A3-10 | AE426 - AE406 | Cooling‐Coil Total Load (kWh/h) | 0.2 | 1.02 | 0.52995 | Within range
D23 | Air-side equipment | A3-11 | AE205 | Cooling‐Coil Sensible Load (kWh/h) | 1.82 | 2.01 | 1.9399 | Within range
D23 | Air-side equipment | A3-11 | AE245 - AE205 | Cooling‐Coil Sensible Load (kWh/h) | 0.2 | 0.39 | 0.28605 | Within range
D23 | Air-side equipment | A3-11 | AE206 | Cooling‐Coil Sensible Load (kWh/h) | 1.62 | 1.79 | 1.706 | Within range
D23 | Air-side equipment | A3-11 | AE226‐206 | Cooling‐Coil Sensible Load (kWh/h) | -0.23 | -0.06 | -0.18816 | Within range
D23 | Air-side equipment | A3-11 | AE305 | Cooling‐Coil Sensible Load (kWh/h) | 8.77 | 9.85 | 9.0986 | Within range
D23 | Air-side equipment | A3-11 | AE305 - AE405 | Cooling‐Coil Sensible Load (kWh/h) | 4.55 | 5.75 | 4.8169 | Within range
D23 | Air-side equipment | A3-11 | AE345 - AE305 | Cooling‐Coil Sensible Load (kWh/h) | -0.15 | 0.79 | 0.45455 | Within range
D23 | Air-side equipment | A3-11 | AE345 - AE445 | Cooling‐Coil Sensible Load (kWh/h) | 4.76 | 6.01 | 5.2217 | Within range
D23 | Air-side equipment | A3-11 | AE306 | Cooling‐Coil Sensible Load (kWh/h) | 8.3 | 9.37 | 8.5573 | Within range
D23 | Air-side equipment | A3-11 | AE306 - AE406 | Cooling‐Coil Sensible Load (kWh/h) | 4.64 | 5.73 | 4.8788 | Within range
D23 | Air-side equipment | A3-11 | AE326 - AE306 | Cooling‐Coil Sensible Load (kWh/h) | -0.91 | -0.01 | -0.50466 | Within range
D23 | Air-side equipment | A3-11 | AE326 - AE426 | Cooling‐Coil Sensible Load (kWh/h) | 4.27 | 5.31 | 4.4315 | Within range
D23 | Air-side equipment | A3-11 | AE405 | Cooling‐Coil Sensible Load (kWh/h) | 3.9 | 4.31 | 4.2817 | Within range
D23 | Air-side equipment | A3-11 | AE445 - AE405 | Cooling‐Coil Sensible Load (kWh/h) | -0.15 | 0.26 | 0.049707 | Within range
D23 | Air-side equipment | A3-11 | AE406 | Cooling‐Coil Sensible Load (kWh/h) | 3.45 | 3.82 | 3.6785 | Within range
D23 | Air-side equipment | A3-11 | AE426 - AE406 | Cooling‐Coil Sensible Load (kWh/h) | -0.22 | 0.14 | -0.057298 | Within range
D23 | Air-side equipment | A3-12 | AE301 | Zone 1 Reheat‐Coil Load (kWh/h) | 7.23 | 8.1 | 7.4229 | Within range
D23 | Air-side equipment | A3-12 | AE401 | Zone 1 Reheat‐Coil Load (kWh/h) | 4.27 | 4.72 | 4.4332 | Within range
D23 | Air-side equipment | A3-12 | AE301 - AE401 | Zone 1 Reheat‐Coil Load (kWh/h) | 2.7 | 3.6 | 2.9897 | Within range
D23 | Air-side equipment | A3-12 | AE305 | Zone 1 Reheat‐Coil Load (kWh/h) | 1.92 | 2.46 | 2.1645 | Within range
D23 | Air-side equipment | A3-12 | AE345 - AE305 | Zone 1 Reheat‐Coil Load (kWh/h) | -0.11 | 0.11 | -0.0085053 | Within range
D23 | Air-side equipment | A3-12 | AE306 | Zone 1 Reheat‐Coil Load (kWh/h) | 1.92 | 2.48 | 2.1893 | Within range
D23 | Air-side equipment | A3-12 | AE326 - AE306 | Zone 1 Reheat‐Coil Load (kWh/h) | -0.11 | 0.11 | 5.8617e-06 | Within range
D23 | Air-side equipment | A3-12 | AE405 | Zone 1 Reheat‐Coil Load (kWh/h) | 0 | 0 | 0 | Skipped
D23 | Air-side equipment | A3-12 | AE406 | Zone 1 Reheat‐Coil Load (kWh/h) | 0 | 0 | 0 | Skipped
D23 | Air-side equipment | A3-13 | AE301 | Zone 2 Reheat‐Coil Load (kWh/h) | 7.77 | 8.81 | 8.0349 | Within range
D23 | Air-side equipment | A3-13 | AE401 | Zone 2 Reheat‐Coil Load (kWh/h) | 4.63 | 5.12 | 4.8171 | Within range
D23 | Air-side equipment | A3-13 | AE301 - AE401 | Zone 2 Reheat‐Coil Load (kWh/h) | 2.87 | 3.93 | 3.2178 | Within range
D23 | Air-side equipment | A3-13 | AE305 | Zone 2 Reheat‐Coil Load (kWh/h) | 2.02 | 2.71 | 2.3392 | Within range
D23 | Air-side equipment | A3-13 | AE345 - AE305 | Zone 2 Reheat‐Coil Load (kWh/h) | -0.12 | 0.12 | -0.011064 | Within range
D23 | Air-side equipment | A3-13 | AE306 | Zone 2 Reheat‐Coil Load (kWh/h) | 2.02 | 2.74 | 2.3705 | Within range
D23 | Air-side equipment | A3-13 | AE326 - AE306 | Zone 2 Reheat‐Coil Load (kWh/h) | -0.12 | 0.12 | 5.8617e-06 | Within range
D23 | Air-side equipment | A3-13 | AE405 | Zone 2 Reheat‐Coil Load (kWh/h) | 0 | 0 | 0 | Skipped
D23 | Air-side equipment | A3-13 | AE406 | Zone 2 Reheat‐Coil Load (kWh/h) | 0 | 0 | 0 | Skipped